## SET A - GSW Cypress
Material Name | Material Type | Material Size | Specification | Quantity | Unit | Plan Sheet Reference | Confidence
PVC Water Main Pipe | Pipe | 8" | GSWC Std. Dwg. P-13; AWWA C900 | 530.22 | LF | P-1, CN-31; STA 0+00.00–5+30.22 | High
Mechanical Joint Resilient Wedge Gate Valve with Valve Box Type 3 | Valve | 8" | GSWC Std. Dwg. P-32, P-43 | 2 | EA | P-1, CN-32; STA 0+20.22, 5+30.22 | High
Flanged End x Mechanical Joint Resilient Wedge Gate Valve with Valve Box Type 3 | Valve | 8" | GSWC Std. Dwg. P-32, P-43 | 0 | EA | P-1, CN-22; no plan callout | High
Wet Barrel Fire Hydrant Assembly with 2-1/2" and 4" Outlets and Tracer Wire Junction Box | Fire Hydrant | 6" | GSWC Std. Dwg. P-8 | 2 | EA | T-1; P-1, CN-33; STA 0+20.22, 5+30.22 | High
Fire Hydrant Branch Tee | Fitting | 6" x 4" x 2-1/2" | GSWC Std. Dwg. P-18 | 2 | EA | P-1; STA 0+20.22, 5+30.22 | High
90° Mechanical Joint Ductile Iron Bend with Thrust Block | Fitting | 8" | GSWC Std. Dwg. P-18 | 1 | EA | P-1, CN-44; STA 5+30.22 | High
Mechanical Joint Ductile Iron Reducer with Thrust Block | Fitting | 8" x 8" | GSWC Std. Dwg. P-18 | 0 | EA | P-1, CN-45; no plan callout | High
Mechanical Joint Ductile Iron Reducer with Thrust Block | Fitting | 8" x 6" | GSWC Std. Dwg. P-18 | 0 | EA | P-1, CN-47; no plan callout | High
Mechanical Joint Ductile Iron Reducing Tee with Thrust Block | Fitting | 8" x 6" | GSWC Std. Dwg. P-18 | 2 | EA | P-1, CN-48; STA 2+11.00, 3+33.61 | High
Tapping Sleeve with 8" Flanged End x MJ Tapping Valve and Thrust Block | Fitting | 12" x 8" | GSWC Std. Dwg. P-18, P-23 | 1 | EA | P-1, CN-88; STA 0+00.00 | High
1" Domestic Water Service Assembly | Service Assembly | 1" | GSWC Std. Dwg. P-25, P-26 | 20 | EA | T-1; P-1, CN-100; callouts 100-1 thru 100-20 | High
1" Irrigation Water Service Assembly | Service Assembly | 1" | GSWC Std. Dwg. P-25, P-26, P-35A | 2 | EA | P-1, CN-101; STA 2+26.40, 3+18.21 | High
6" Fire Water Service Assembly | Service Assembly | 6" | GSWC Std. Dwg. P-35B | 2 | EA | P-1, CN-110; STA 2+11.00, 3+33.61 | High
8" x 6" Mechanical Joint Ductile Iron Reducing Tee at Main | Fitting | 8" x 6" | Detail 1 | 2 | EA | P-1, Detail 1; CN-110 locations | High
Ductile Iron Pipe | Pipe | 6" | AWWA C151 DIP | 90 | LF | P-1; 2 laterals scaled at 1"=20' (~45 LF each) | Medium
Ductile Iron Pipe | Pipe | 4" | AWWA C151 DIP | QUANTITY_REQUIRED | LF | P-1, Detail 1; tee-to-SS run not dimensioned | Low
Outside Screw and Yoke Resilient Wedge Gate Valve | Valve | 6" | AWWA C509 | 2 | EA | P-1, Detail 1; per CN-110 location | High
Post Indicator Valve | Valve | 6" | USC approved | 2 | EA | P-1, Detail 1; per CN-110 location | High
Double Check Detector Assembly | Backflow Assembly | 6" | USC approved | 2 | EA | P-1, Detail 1; per CN-110 location | High
Mechanical Joint Ductile Iron Tee | Fitting | 6" x 6" x 4" | AWWA C151 | 2 | EA | P-1, Detail 1; per CN-110 location | High
90° Mechanical Joint Ductile Iron Bend | Fitting | 4" | AWWA C151 | 2 | EA | P-1, Detail 1; per CN-110 location | High
Mechanical Joint Ductile Iron Tee | Fitting | 4" | AWWA C151 | 2 | EA | P-1, Detail 1; per CN-110 location | High
Stainless Steel Pipe | Pipe | 4" | U.L. listed riser connection | 10 | LF | P-1, Detail 1; 5'-0" MIN x 2 locations | High
U.L. Listed In-Building Stainless Steel Riser Sweep | Fitting | 4" | U.L. listed | 2 | EA | P-1, Detail 1; per CN-110 location | High
Link-Seal Pipe Penetration Seal System | Seal | 2" annular space | Building entry detail | 2 | EA | P-1, Detail 1; per CN-110 location | High
Reduced Pressure Principal Backflow Assembly (Lead Free) | Backflow Assembly | 1" | GSWC Std. Dwg. P-25A | 2 | EA | T-1, GN-20; per CN-101 location | High
8 mil Polyethylene Pipe Encasement | Pipe Wrap | 8 mil | AWWA C105 | 48 | LF | T-1, GN-8; 12 metallic appurtenances x 4 LF avg | Medium
Concrete Thrust Block | Concrete | Per GSWC P-18 | CN-44, CN-48, CN-88 | 6 | EA | P-1; 1 bend + 2 tees + 1 tap + 2 FS connections | Medium
No. 3 Sand Pipe Bedding | Bedding | No. 3 sand | Cypress Std. Plan 324 Case I | QUANTITY_REQUIRED | CY | D-1; trench width not dimensioned on plans | Low
Crushed Rock Pipe Bedding | Bedding | 3/4" D | Cypress Std. Plan 324 Case I | QUANTITY_REQUIRED | CY | D-1; trench width not dimensioned on plans | Low
Class A Concrete | Concrete | Class A | Cypress Std. Plan 324 Case V | QUANTITY_REQUIRED | CY | D-1; no pipe segments designated Case V | Low
Class B Concrete | Concrete | Class B | Cypress Std. Plan 324 | QUANTITY_REQUIRED | CY | D-1; trench width not dimensioned on plans | Low
Asphalt Concrete Pavement | Paving | AC | Cypress Std. Plan 109 | QUANTITY_REQUIRED | SY | D-1; restoration area not quantified on P-1 | Low
Slurry Seal | Paving | Slurry seal | Cypress Std. Plan 109 | QUANTITY_REQUIRED | SY | D-1; restoration area not quantified on P-1 | Low

## SET B - Whittier Water
Material Name | Material Type | Material Size | Specification | Quantity | Unit | Plan Sheet Reference | Confidence
Ductile Iron Water Pipe | Pipe | 4" | Class 350, C104; Whittier Std. W-603; W-647 trench | 33 | LF | Sheet 2, Item 1 | High
Ductile Iron Water Pipe | Pipe | 6" | Class 350, C104; Whittier Std. W-603; W-647 trench | 25 | LF | Sheet 2, Item 2 | High
Mechanical Joint Gate Valve and Assembly | Valve | 4" | Whittier Std. W-620 | 1 | EA | Sheet 2, Item 3; Sheet 3, CN-3 | High
Mechanical Joint Gate Valve and Assembly | Valve | 6" | Whittier Std. W-620 | 1 | EA | Sheet 2, Item 4; Sheet 3, CN-4 | High
1" Water Service with Meter and Box | Service Assembly | 1" | Whittier Std. W-601 | 1 | EA | Sheet 2, Item 5; Sheet 3, CN-5 | High
Mechanical Joint Ductile Iron Tee | Fitting | 8" x 8" x 4" | Whittier Std. W-649 cut-in | 1 | EA | Sheet 2, Item 6; Sheet 3, CN-6 | High
Mechanical Joint Ductile Iron Tee | Fitting | 8" x 8" x 6" | Whittier Std. W-649 cut-in | 1 | EA | Sheet 2, Item 7; Sheet 3, CN-7 | High
FEBCO LF860 Reduced Pressure Backflow Preventer | Backflow Preventer | 1" | Whittier Std. W-610 | 1 | EA | Sheet 2, Item 8; Sheet 3, CN-8 | High
4" Underground Water Meter Assembly | Meter Assembly | 4" | Whittier Std. W-605 | 1 | EA | Sheet 2, Item 9; Sheet 3, CN-9 | High
FEBCO MasterSeries LF876V Fire Line Double Check Detector Assembly with Bypass Meter | Backflow Assembly | 6" | Whittier Std. W-606 | 1 | EA | Sheet 2, Item 10; Sheet 3, CN-10 | High
FEBCO LF860 Reduced Pressure Backflow Preventer | Backflow Preventer | 4" | Whittier Std. W-611 | 1 | EA | Sheet 2, Item 13; Sheet 3, CN-13 | High
Pipe Joint Restraint System | Restraint | Per pipe size | Whittier Std. W-636 | 2 | EA | Sheet 2, Item 12; Sheet 3, CN-12 | High
Type K Copper Water Service Tubing | Tubing | 1" minimum | Water Note 11 | 30 | LF | Sheet 3; 25' CL-to-curb + 5' to assembly | Medium
Eagle Loc Internal Pipe Restraint | Restraint | Per pipe size | Water Note 13 | 2 | EA | Sheet 2, Item 12 | High
EBBA Iron Megalug MJ Fitting Restraint Adapter | Restraint | Per fitting size | Water Note 13 | 4 | EA | Sheet 2/3; 2 tees + 2 gate valves | High
Concrete Thrust Block | Concrete | Per W-636 | Water Note 13 | QUANTITY_REQUIRED | CY | W-636 detail not in plan set | Low
Sand Pipe Bedding and Shading | Bedding | Per W-647 | General Note 41 | QUANTITY_REQUIRED | CY | W-647 trench detail not in plan set | Low
Slurry Backfill | Backfill | Slurry | General Note 41 | QUANTITY_REQUIRED | CY | W-647 trench detail not in plan set | Low
Crushed Miscellaneous Base | Base | CMB | General Note 38 | QUANTITY_REQUIRED | CY | No restoration area quantified | Low
Asphalt Concrete Pavement Restoration | Paving | AC | General notes | QUANTITY_REQUIRED | SY | No pavement restoration area quantified | Low
Concrete Curb, Gutter, and Sidewalk Repair | Concrete | Per City standard | General notes | QUANTITY_REQUIRED | LF | No curb/gutter repair lengths quantified | Low

## SET C - Tract 82457 Sewer
Material Name | Material Type | Material Size | Specification | Quantity | Unit | Plan Sheet Reference | Confidence
Extra Strength Vitrified Clay Sewer Pipe | Pipe | 8" | CN-16; Type D/G joints SPPWC 208-2 | 802.84 | LF | PC 12447 Page 2 Profile; 272.78+183.47+164.57+132.02+50.00 | High
Vitrified Clay Pipe Joint | Joint | 8" | Type D or G per SPPWC 208-2 | QUANTITY_REQUIRED | EA | Joint spacing not specified on plans | Low
Vitrified Clay House Lateral Assembly Type D | Pipe Assembly | 4" | SPPWC 222-2 Type D | 24 | EA | Page 2 Lots 1–19 (19) + Page 3 Lots 20–24, 21 (5) | High
Vitrified Clay House Lateral Assembly Type C | Pipe Assembly | 4" | SPPWC 222-2 Type C | 6 | EA | Page 3 Lots 25–30 | High
8" x 4" Vitrified Clay Wye Fitting | Fitting | 8" x 4" | "USE 8"x4" WYE ONLY" CN-6 | 30 | EA | 1 per lateral; 19+11 lots | High
Precast Concrete Sewer Manhole | Manhole | QUANTITY_REQUIRED | SPPWC 200-3; LACPW 2023-2 Case II | 4 | EA | Page 2 Profile STA 8+02.38, 5+30.06, 3+46.59, 1+82.02 | High
Cast Iron Manhole Frame and Cover, Locking Type | Manhole Appurtenance | Per SPPWC 210-3 | CN-17 | 4 | EA | 1 per new manhole | High
Standard Manhole Step | Manhole Appurtenance | LACPW 2015-1 | Per standard | QUANTITY_REQUIRED | EA | Step count per depth not shown | Low
Terminal Cleanout Structure with Frame and Cover | Structure | SPPWC 204-2 | CN-19 | QUANTITY_REQUIRED | EA | No cleanout symbols counted on plans | Low
Neoprene Bushing for Type D Rubber Sleeve Joint | Joint Accessory | Type D | CN-4 | QUANTITY_REQUIRED | EA | No cast-iron-to-VCP connections counted | Low
Concrete Encasement for VCP Sewer | Concrete | LACPW 2023-2 Case II | CN-7 | QUANTITY_REQUIRED | CY | Encasement lengths not flagged on profile | Low
Proposed Water Main Pipe | Pipe | 8" | "PROP. 8" WATER" | 802.84 | LF | Page 2; parallel to 8" VCP alignment | Medium
Proposed Storm Drain Pipe | Pipe | 12" | "PROP. 12" SD" | QUANTITY_REQUIRED | LF | Page 2; crossing shown, no labeled run length | Low
Proposed Storm Drain Pipe | Pipe | 24" | "PROP. 24" SD" | 320.4 | LF | Page 3; 55.0+55.0+56.0+60.7+93.7 | High
Backwater Valve | Valve | Per Plumbing Code 710 | Lots 26 and 27 | 2 | EA | Sheet 1 Stormwater Notes | High
Sewer Pipe Bedding Material | Bedding | SPPWC 2021-1 | Standard Plans | QUANTITY_REQUIRED | CY | SPPWC 2021-1 detail not in plan set | Low
Pipe Cradling and Encasement Material | Encasement | SPPWC 2023-2 | Standard Plans | QUANTITY_REQUIRED | CY | Encasement lengths not flagged | Low
Blanket Protection for Pipes | Pipe Protection | SPPWC 225-2 | Standard Plans | QUANTITY_REQUIRED | LF | No pipe protection zones flagged | Low
Trench Backfill / Fill Material | Backfill | 90% compaction | CN-11 | QUANTITY_REQUIRED | CY | Trench dimensions not on plans | Low
Asphalt Concrete Trench Resurfacing | Paving | AC | CN-9 | QUANTITY_REQUIRED | SY | Paved trench length not quantified | Low
Wye or Tee Support | Support | LACPW 2024-1 | Standard Plans | 30 | EA | 1 per lateral connection | Medium
Pipe Anchor and Backfill Stabilizer | Anchor | SPPWC 221-2 | Standard Plans | QUANTITY_REQUIRED | EA | No anchor callouts on plans | Low
Ductile Iron Pipe with Protecto 401 Ceramic Epoxy Lining | Pipe (Alternate) | 8" | CN-16 alternate | 0 | LF | Alternate; VCP is base bid | High
Cured-In-Place Pipe Liner | Pipe Liner (Alternate) | — | CN-18 alternate | 0 | LF | Alternate; not base bid | High